## Form-23 Measurements
FORM No. 23 - MEASUREMENT BOOK
GOVERNMENT OF MAHARASHTRA ¦ PUBLIC WORKS DEPARTMENT (ELECTRICAL WING) ¦ Smart-MB
Name of Work: Electrical Installation to New Academic Building - Zilla Parishad High School, Sinnar
Project Code: PWDE/ELE/NASHIK/2024-25/017 ¦ Estimate No: EST/ELE/NSK/2024-25/017 ¦ TS No: TS/ELE/NSK/2024-25/041 dt. 19/08/2024
MB No: MB-01 ¦ Agreement: AG/ELE/NSK/2024-25/009 ¦ Agency: M/s Vidarbha Electricals Pvt. Ltd. ¦ CSR: 2024-25 / Nashik
Tendered (estimate) amount: Rs. 13,56,630 ¦ Prepared: 01/10/2026 18:17
Item No. | CSR Code | Description of Item (Master CSR) | Location / Room | Floor | Unit | No. | Length | Breadth | Height | Quantity | Rate | Amount | Measured On | Status
1 | 1-9-1 | Concealed type light / fan / bell point wiring with 1.5 sq.mm (1.5 + 1E) FR grade copper wire in provided concealed pipes, terminating on modular accessories in box, including earthing and required accessories as per specification No: WG-PW/CW. | Head Master Cabin | Ground Floor | Point | 15 | 1 | 0 | 0 | 15 | 495 | 7425 | 18/01/2025 | submitted
1 | 1-9-1 | Concealed type light / fan / bell point wiring with 1.5 sq.mm (1.5 + 1E) FR grade copper wire in provided concealed pipes, terminating on modular accessories in box, including earthing and required accessories as per specification No: WG-PW/CW. | Office Room 1 | Ground Floor | Point | 68 | 1 | 0 | 0 | 68 | 495 | 33660 | 18/01/2025 | submitted
2 | 1-9-2 | Concealed type independent plug point wiring with 2.5 sq.mm (2.5 + 1E) FR grade copper wire in provided concealed pipes with modular socket, switch and earthing as per specification No: WG-PW/CW. | Head Master Cabin | Ground Floor | Point | 12 | 1 | 0 | 0 | 12 | 605 | 7260 | 18/01/2025 | submitted
2 | 1-9-2 | Concealed type independent plug point wiring with 2.5 sq.mm (2.5 + 1E) FR grade copper wire in provided concealed pipes with modular socket, switch and earthing as per specification No: WG-PW/CW. | Office Room 1 | Ground Floor | Point | 6 | 1 | 0 | 0 | 6 | 605 | 3630 | 18/01/2025 | submitted
2 | 1-9-2 | Concealed type independent plug point wiring with 2.5 sq.mm (2.5 + 1E) FR grade copper wire in provided concealed pipes with modular socket, switch and earthing as per specification No: WG-PW/CW. | Office Room 2 | Ground Floor | Point | 2 | 1 | 0 | 0 | 2 | 605 | 1210 | 18/01/2025 | submitted
2 | 1-9-2 | Concealed type independent plug point wiring with 2.5 sq.mm (2.5 + 1E) FR grade copper wire in provided concealed pipes with modular socket, switch and earthing as per specification No: WG-PW/CW. | Store Room | Ground Floor | Point | 2 | 1 | 0 | 0 | 2 | 605 | 1210 | 18/01/2025 | submitted
3 | 1-9-3 | Concealed type 6 A plug point wiring with 1.5 sq.mm (2 + 1E) FRLSH copper wire, modular accessories, box and earthing as per specification No: WG-PW/CW. | Head Master Cabin | Ground Floor | Point | 2 | 1 | 0 | 0 | 2 | 540 | 1080 | 18/01/2025 | submitted
3 | 1-9-3 | Concealed type 6 A plug point wiring with 1.5 sq.mm (2 + 1E) FRLSH copper wire, modular accessories, box and earthing as per specification No: WG-PW/CW. | Office Room 1 | Ground Floor | Point | 6 | 1 | 0 | 0 | 6 | 540 | 3240 | 18/01/2025 | submitted
3 | 1-9-3 | Concealed type 6 A plug point wiring with 1.5 sq.mm (2 + 1E) FRLSH copper wire, modular accessories, box and earthing as per specification No: WG-PW/CW. | Office Room 2 | Ground Floor | Point | 2 | 1 | 0 | 0 | 2 | 540 | 1080 | 18/01/2025 | submitted
3 | 1-9-3 | Concealed type 6 A plug point wiring with 1.5 sq.mm (2 + 1E) FRLSH copper wire, modular accessories, box and earthing as per specification No: WG-PW/CW. | Store Room | Ground Floor | Point | 8 | 1 | 0 | 0 | 8 | 540 | 4320 | 18/01/2025 | submitted
4 | 1-9-4 | Concealed type twin light point / two way control point wiring with 1.5 sq.mm (3 + 1E) FR copper wire, two modular switches, box, earthing and accessories as per specification No: WG-PW/CW. | Head Master Cabin | Ground Floor | Point | 3 | 1 | 0 | 0 | 3 | 765 | 2295 | 18/01/2025 | submitted
4 | 1-9-4 | Concealed type twin light point / two way control point wiring with 1.5 sq.mm (3 + 1E) FR copper wire, two modular switches, box, earthing and accessories as per specification No: WG-PW/CW. | Office Room 1 | Ground Floor | Point | 2 | 1 | 0 | 0 | 2 | 765 | 1530 | 18/01/2025 | submitted
4 | 1-9-4 | Concealed type twin light point / two way control point wiring with 1.5 sq.mm (3 + 1E) FR copper wire, two modular switches, box, earthing and accessories as per specification No: WG-PW/CW. | Office Room 2 | Ground Floor | Point | 2 | 1 | 0 | 0 | 2 | 765 | 1530 | 18/01/2025 | submitted
4 | 1-9-4 | Concealed type twin light point / two way control point wiring with 1.5 sq.mm (3 + 1E) FR copper wire, two modular switches, box, earthing and accessories as per specification No: WG-PW/CW. | Store Room | Ground Floor | Point | 3 | 1 | 0 | 0 | 3 | 765 | 2295 | 18/01/2025 | submitted
4 | 1-9-4 | Concealed type twin light point / two way control point wiring with 1.5 sq.mm (3 + 1E) FR copper wire, two modular switches, box, earthing and accessories as per specification No: WG-PW/CW. | Class Room 1 | First Floor | Point | 2 | 1 | 0 | 0 | 2 | 765 | 1530 | 18/01/2025 | submitted
5 | 1-9-5 | Concealed type 16 A power plug point wiring with 4.0 sq.mm (2 + 1E) FRLSH copper wire, modular socket with switch, box and earthing as per specification No: WG-PW/CW. | Head Master Cabin | Ground Floor | Point | 2 | 1 | 0 | 0 | 2 | 830 | 1660 | 18/01/2025 | submitted
5 | 1-9-5 | Concealed type 16 A power plug point wiring with 4.0 sq.mm (2 + 1E) FRLSH copper wire, modular socket with switch, box and earthing as per specification No: WG-PW/CW. | Office Room 1 | Ground Floor | Point | 4 | 1 | 0 | 0 | 4 | 830 | 3320 | 18/01/2025 | submitted
5 | 1-9-5 | Concealed type 16 A power plug point wiring with 4.0 sq.mm (2 + 1E) FRLSH copper wire, modular socket with switch, box and earthing as per specification No: WG-PW/CW. | Office Room 2 | Ground Floor | Point | 3 | 1 | 0 | 0 | 3 | 830 | 2490 | 18/01/2025 | submitted
6 | 1-9-6 | Concealed type ceiling fan point wiring with 1.5 sq.mm (2 + 1E) FR copper wire, fan hook / clamp box on RCC slab, modular regulator, earthing and accessories as per specification No: WG-PW/CW. | Head Master Cabin | Ground Floor | Point | 9 | 1 | 0 | 0 | 9 | 630 | 5670 | 18/01/2025 | submitted
6 | 1-9-6 | Concealed type ceiling fan point wiring with 1.5 sq.mm (2 + 1E) FR copper wire, fan hook / clamp box on RCC slab, modular regulator, earthing and accessories as per specification No: WG-PW/CW. | Office Room 1 | Ground Floor | Point | 2 | 1 | 0 | 0 | 2 | 630 | 1260 | 18/01/2025 | submitted
6 | 1-9-6 | Concealed type ceiling fan point wiring with 1.5 sq.mm (2 + 1E) FR copper wire, fan hook / clamp box on RCC slab, modular regulator, earthing and accessories as per specification No: WG-PW/CW. | Office Room 2 | Ground Floor | Point | 5 | 1 | 0 | 0 | 5 | 630 | 3150 | 18/01/2025 | submitted
7 | 1-9-8 | Concealed type call bell point wiring with 1.5 sq.mm (2 + 1E) FR copper wire, bell push and earthing in concealed box as per specification No: WG-PW/CW. | Head Master Cabin | Ground Floor | Point | 1 | 1 | 0 | 0 | 1 | 390 | 390 | 18/01/2025 | submitted
7 | 1-9-8 | Concealed type call bell point wiring with 1.5 sq.mm (2 + 1E) FR copper wire, bell push and earthing in concealed box as per specification No: WG-PW/CW. | Office Room 1 | Ground Floor | Point | 1 | 1 | 0 | 0 | 1 | 390 | 390 | 18/01/2025 | submitted
7 | 1-9-8 | Concealed type call bell point wiring with 1.5 sq.mm (2 + 1E) FR copper wire, bell push and earthing in concealed box as per specification No: WG-PW/CW. | Office Room 2 | Ground Floor | Point | 1 | 1 | 0 | 0 | 1 | 390 | 390 | 18/01/2025 | submitted
7 | 1-9-8 | Concealed type call bell point wiring with 1.5 sq.mm (2 + 1E) FR copper wire, bell push and earthing in concealed box as per specification No: WG-PW/CW. | Store Room | Ground Floor | Point | 1 | 1 | 0 | 0 | 1 | 390 | 390 | 18/01/2025 | submitted
8 | 1-9-10 | Supplying and fixing modular electronic fan regulator with 2 M plate, GI box, connections and earthing complete as per specification No: WG-PS/MOD. | Head Master Cabin | Ground Floor | Each | 8 | 1 | 0 | 0 | 8 | 435 | 3480 | 18/01/2025 | submitted
8 | 1-9-10 | Supplying and fixing modular electronic fan regulator with 2 M plate, GI box, connections and earthing complete as per specification No: WG-PS/MOD. | Office Room 1 | Ground Floor | Each | 7 | 1 | 0 | 0 | 7 | 435 | 3045 | 18/01/2025 | submitted
9 | 1-1-1 | Supplying and laying 20 mm dia. PVC conduit concealed in wall / ceiling / slab with necessary bends, couplers, junction boxes, cutting and making good the wall complete as per specification No: WG-CP/PVC. | Head Master Cabin | Ground Floor | m | 1 | 204.47 | 0 | 0 | 204.47 | 100 | 20447 | 18/01/2025 | submitted
9 | 1-1-1 | Supplying and laying 20 mm dia. PVC conduit concealed in wall / ceiling / slab with necessary bends, couplers, junction boxes, cutting and making good the wall complete as per specification No: WG-CP/PVC. | Office Room 1 | Ground Floor | m | 1 | 215.24 | 0 | 0 | 215.24 | 100 | 21524 | 18/01/2025 | submitted
9 | 1-1-1 | Supplying and laying 20 mm dia. PVC conduit concealed in wall / ceiling / slab with necessary bends, couplers, junction boxes, cutting and making good the wall complete as per specification No: WG-CP/PVC. | Office Room 2 | Ground Floor | m | 1 | 170.71 | 0 | 0 | 170.71 | 100 | 17071 | 18/01/2025 | submitted
10 | 1-1-2 | Supplying and laying 25 mm dia. PVC conduit concealed in wall / ceiling / slab with necessary bends, couplers, junction boxes, cutting and making good the wall complete as per specification No: WG-CP/PVC. | Head Master Cabin | Ground Floor | m | 1 | 38.28 | 0 | 0 | 38.28 | 125 | 4785 | 18/01/2025 | submitted
10 | 1-1-2 | Supplying and laying 25 mm dia. PVC conduit concealed in wall / ceiling / slab with necessary bends, couplers, junction boxes, cutting and making good the wall complete as per specification No: WG-CP/PVC. | Office Room 1 | Ground Floor | m | 1 | 101.81 | 0 | 0 | 101.81 | 125 | 12726.25 | 18/01/2025 | submitted
10 | 1-1-2 | Supplying and laying 25 mm dia. PVC conduit concealed in wall / ceiling / slab with necessary bends, couplers, junction boxes, cutting and making good the wall complete as per specification No: WG-CP/PVC. | Office Room 2 | Ground Floor | m | 1 | 75.39 | 0 | 0 | 75.39 | 125 | 9423.75 | 18/01/2025 | submitted
10 | 1-1-2 | Supplying and laying 25 mm dia. PVC conduit concealed in wall / ceiling / slab with necessary bends, couplers, junction boxes, cutting and making good the wall complete as per specification No: WG-CP/PVC. | Store Room | Ground Floor | m | 1 | 37.77 | 0 | 0 | 37.77 | 125 | 4721.25 | 18/01/2025 | submitted
10 | 1-1-2 | Supplying and laying 25 mm dia. PVC conduit concealed in wall / ceiling / slab with necessary bends, couplers, junction boxes, cutting and making good the wall complete as per specification No: WG-CP/PVC. | Class Room 1 | First Floor | m | 1 | 74.26 | 0 | 0 | 74.26 | 125 | 9282.5 | 18/01/2025 | submitted
11 | 1-1-4 | Supplying and laying 20 mm dia. 16 gauge rigid steel conduit on surface / concealed with couplers, bends, hooks, saddles, painting with two coats of anti-corrosive paint, earthing continuity complete as per specification No: WG-CP/RSC. | Head Master Cabin | Ground Floor | m | 1 | 52.18 | 0 | 0 | 52.18 | 275 | 14349.5 | 18/01/2025 | submitted
11 | 1-1-4 | Supplying and laying 20 mm dia. 16 gauge rigid steel conduit on surface / concealed with couplers, bends, hooks, saddles, painting with two coats of anti-corrosive paint, earthing continuity complete as per specification No: WG-CP/RSC. | Office Room 1 | Ground Floor | m | 1 | 37.34 | 0 | 0 | 37.34 | 275 | 10268.5 | 18/01/2025 | submitted
11 | 1-1-4 | Supplying and laying 20 mm dia. 16 gauge rigid steel conduit on surface / concealed with couplers, bends, hooks, saddles, painting with two coats of anti-corrosive paint, earthing continuity complete as per specification No: WG-CP/RSC. | Office Room 2 | Ground Floor | m | 1 | 84.82 | 0 | 0 | 84.82 | 275 | 23325.5 | 18/01/2025 | submitted
12 | 1-1-6 | Supplying and fixing GI concealed box (8 module) with cover plate for modular switches / sockets including cutting and making good complete as per specification No: WG-CP/MOD. | Head Master Cabin | Ground Floor | Each | 2 | 1 | 0 | 0 | 2 | 220 | 440 | 18/01/2025 | submitted
12 | 1-1-6 | Supplying and fixing GI concealed box (8 module) with cover plate for modular switches / sockets including cutting and making good complete as per specification No: WG-CP/MOD. | Office Room 1 | Ground Floor | Each | 6 | 1 | 0 | 0 | 6 | 220 | 1320 | 18/01/2025 | submitted
12 | 1-1-6 | Supplying and fixing GI concealed box (8 module) with cover plate for modular switches / sockets including cutting and making good complete as per specification No: WG-CP/MOD. | Office Room 2 | Ground Floor | Each | 34 | 1 | 0 | 0 | 34 | 220 | 7480 | 18/01/2025 | submitted
12 | 1-1-6 | Supplying and fixing GI concealed box (8 module) with cover plate for modular switches / sockets including cutting and making good complete as per specification No: WG-CP/MOD. | Store Room | Ground Floor | Each | 12 | 1 | 0 | 0 | 12 | 220 | 2640 | 18/01/2025 | submitted
12 | 1-1-6 | Supplying and fixing GI concealed box (8 module) with cover plate for modular switches / sockets including cutting and making good complete as per specification No: WG-CP/MOD. | Class Room 1 | First Floor | Each | 61 | 1 | 0 | 0 | 61 | 220 | 13420 | 18/01/2025 | submitted
13 | 1-3-3 | Supplying and erecting mains with 2 x 4 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Head Master Cabin | Ground Floor | m | 1 | 32.1 | 0 | 0 | 32.1 | 150 | 4815 | 18/01/2025 | submitted
13 | 1-3-3 | Supplying and erecting mains with 2 x 4 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Office Room 1 | Ground Floor | m | 1 | 36.9 | 0 | 0 | 36.9 | 150 | 5535 | 18/01/2025 | submitted
13 | 1-3-3 | Supplying and erecting mains with 2 x 4 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Office Room 2 | Ground Floor | m | 1 | 21.64 | 0 | 0 | 21.64 | 150 | 3246 | 18/01/2025 | submitted
13 | 1-3-3 | Supplying and erecting mains with 2 x 4 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Store Room | Ground Floor | m | 1 | 29.45 | 0 | 0 | 29.45 | 150 | 4417.5 | 18/01/2025 | submitted
13 | 1-3-3 | Supplying and erecting mains with 2 x 4 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Class Room 1 | First Floor | m | 1 | 130.71 | 0 | 0 | 130.71 | 150 | 19606.5 | 18/01/2025 | submitted
14 | 1-3-6 | Supplying and erecting mains with 3 x 4 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Head Master Cabin | Ground Floor | m | 1 | 136.91 | 0 | 0 | 136.91 | 220 | 30120.2 | 18/01/2025 | submitted
14 | 1-3-6 | Supplying and erecting mains with 3 x 4 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Office Room 1 | Ground Floor | m | 1 | 46.32 | 0 | 0 | 46.32 | 220 | 10190.4 | 18/01/2025 | submitted
15 | 1-3-8 | Supplying and erecting mains with 3 x 10 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Head Master Cabin | Ground Floor | m | 1 | 16.93 | 0 | 0 | 16.93 | 460 | 7787.8 | 18/01/2025 | submitted
15 | 1-3-8 | Supplying and erecting mains with 3 x 10 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Office Room 1 | Ground Floor | m | 1 | 32.57 | 0 | 0 | 32.57 | 460 | 14982.2 | 18/01/2025 | submitted
15 | 1-3-8 | Supplying and erecting mains with 3 x 10 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Office Room 2 | Ground Floor | m | 1 | 9.97 | 0 | 0 | 9.97 | 460 | 4586.2 | 18/01/2025 | submitted
15 | 1-3-8 | Supplying and erecting mains with 3 x 10 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Store Room | Ground Floor | m | 1 | 18.3 | 0 | 0 | 18.3 | 460 | 8418 | 18/01/2025 | submitted
15 | 1-3-8 | Supplying and erecting mains with 3 x 10 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Class Room 1 | First Floor | m | 1 | 38.68 | 0 | 0 | 38.68 | 460 | 17792.8 | 18/01/2025 | submitted
16 | 1-3-11 | Supplying and erecting mains with 4 x 10 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Head Master Cabin | Ground Floor | m | 1 | 14.42 | 0 | 0 | 14.42 | 615 | 8868.3 | 18/01/2025 | submitted
16 | 1-3-11 | Supplying and erecting mains with 4 x 10 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Office Room 1 | Ground Floor | m | 1 | 21.92 | 0 | 0 | 21.92 | 615 | 13480.8 | 18/01/2025 | submitted
16 | 1-3-11 | Supplying and erecting mains with 4 x 10 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Office Room 2 | Ground Floor | m | 1 | 5 | 0 | 0 | 5 | 615 | 3075 | 18/01/2025 | submitted
16 | 1-3-11 | Supplying and erecting mains with 4 x 10 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Store Room | Ground Floor | m | 1 | 25.08 | 0 | 0 | 25.08 | 615 | 15424.2 | 18/01/2025 | submitted
16 | 1-3-11 | Supplying and erecting mains with 4 x 10 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | Class Room 1 | First Floor | m | 1 | 21.73 | 0 | 0 | 21.73 | 615 | 13363.95 | 18/01/2025 | submitted
17 | 1-5-5 | Supplying and fixing modular switch 6 A / 16 A on 2 M plate with GI box, connections and earthing complete as per specification No: WG-PS/MOD. | Head Master Cabin | Ground Floor | Each | 6 | 1 | 0 | 0 | 6 | 190 | 1140 | 18/01/2025 | submitted
17 | 1-5-5 | Supplying and fixing modular switch 6 A / 16 A on 2 M plate with GI box, connections and earthing complete as per specification No: WG-PS/MOD. | Office Room 1 | Ground Floor | Each | 26 | 1 | 0 | 0 | 26 | 190 | 4940 | 18/01/2025 | submitted
17 | 1-5-5 | Supplying and fixing modular switch 6 A / 16 A on 2 M plate with GI box, connections and earthing complete as per specification No: WG-PS/MOD. | Office Room 2 | Ground Floor | Each | 20 | 1 | 0 | 0 | 20 | 190 | 3800 | 18/01/2025 | submitted
17 | 1-5-5 | Supplying and fixing modular switch 6 A / 16 A on 2 M plate with GI box, connections and earthing complete as per specification No: WG-PS/MOD. | Store Room | Ground Floor | Each | 9 | 1 | 0 | 0 | 9 | 190 | 1710 | 18/01/2025 | submitted
18 | 1-5-1 | Supplying and erecting recess type 3 pin plug socket 6 A with piano switch 6 A combined unit erected on polished double wooden block / folded sheet box complete as per specification No: WG-PS/RC. | Head Master Cabin | Ground Floor | Each | 6 | 1 | 0 | 0 | 6 | 170 | 1020 | 18/01/2025 | submitted
18 | 1-5-1 | Supplying and erecting recess type 3 pin plug socket 6 A with piano switch 6 A combined unit erected on polished double wooden block / folded sheet box complete as per specification No: WG-PS/RC. | Office Room 1 | Ground Floor | Each | 18 | 1 | 0 | 0 | 18 | 170 | 3060 | 18/01/2025 | submitted
19 | 1-5-2 | Supplying and erecting recess type 6 pin plug socket 16 A with switch 16 A combined unit mounted on sheet steel box with earth terminal complete as per specification No: WG-PS/RC. | Head Master Cabin | Ground Floor | Each | 5 | 1 | 0 | 0 | 5 | 405 | 2025 | 18/01/2025 | submitted
19 | 1-5-2 | Supplying and erecting recess type 6 pin plug socket 16 A with switch 16 A combined unit mounted on sheet steel box with earth terminal complete as per specification No: WG-PS/RC. | Office Room 1 | Ground Floor | Each | 4 | 1 | 0 | 0 | 4 | 405 | 1620 | 18/01/2025 | submitted
20 | 2-1-3 | Supplying and erecting LED batten luminaire 20 W, 4 ft, 6500 K, polycarbonate body with driver, complete with connections and earthing as per specification No: LF-LED/BTN. | Head Master Cabin | Ground Floor | Each | 87 | 1 | 0 | 0 | 87 | 1205 | 104835 | 18/01/2025 | submitted
20 | 2-1-3 | Supplying and erecting LED batten luminaire 20 W, 4 ft, 6500 K, polycarbonate body with driver, complete with connections and earthing as per specification No: LF-LED/BTN. | Office Room 1 | Ground Floor | Each | 8 | 1 | 0 | 0 | 8 | 1205 | 9640 | 18/01/2025 | submitted
21 | 2-1-1 | Supplying and erecting LED panel luminaire 18 W, 1200 x 300 mm, surface mounted, 6500 K, CRCA sheet housing with diffuser, complete with driver, connections and earthing as per specification No: LF-LED/PNL. | Head Master Cabin | Ground Floor | Each | 13 | 1 | 0 | 0 | 13 | 2185 | 28405 | 18/01/2025 | submitted
21 | 2-1-1 | Supplying and erecting LED panel luminaire 18 W, 1200 x 300 mm, surface mounted, 6500 K, CRCA sheet housing with diffuser, complete with driver, connections and earthing as per specification No: LF-LED/PNL. | Office Room 1 | Ground Floor | Each | 29 | 1 | 0 | 0 | 29 | 2185 | 63365 | 18/01/2025 | submitted
22 | 2-1-5 | Supplying and erecting LED bulkhead luminaire 20 W, IP65, die cast aluminium body with toughened glass, complete with driver, connections and earthing as per specification No: LF-LED/BHD. | Head Master Cabin | Ground Floor | Each | 11 | 1 | 0 | 0 | 11 | 1695 | 18645 | 18/01/2025 | submitted
22 | 2-1-5 | Supplying and erecting LED bulkhead luminaire 20 W, IP65, die cast aluminium body with toughened glass, complete with driver, connections and earthing as per specification No: LF-LED/BHD. | Office Room 1 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 1695 | 1695 | 18/01/2025 | submitted
23 | 2-1-9 | Supplying and erecting LED flood light luminaire 100 W, IP66, die cast aluminium housing with toughened glass, surge protection, adjustable bracket, complete with wiring and earthing as per specification No: LF-LED/FL. | Head Master Cabin | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 4365 | 4365 | 18/01/2025 | submitted
23 | 2-1-9 | Supplying and erecting LED flood light luminaire 100 W, IP66, die cast aluminium housing with toughened glass, surge protection, adjustable bracket, complete with wiring and earthing as per specification No: LF-LED/FL. | Office Room 1 | Ground Floor | Each | 3 | 1 | 0 | 0 | 3 | 4365 | 13095 | 18/01/2025 | submitted
23 | 2-1-9 | Supplying and erecting LED flood light luminaire 100 W, IP66, die cast aluminium housing with toughened glass, surge protection, adjustable bracket, complete with wiring and earthing as per specification No: LF-LED/FL. | Office Room 2 | Ground Floor | Each | 3 | 1 | 0 | 0 | 3 | 4365 | 13095 | 18/01/2025 | submitted
23 | 2-1-9 | Supplying and erecting LED flood light luminaire 100 W, IP66, die cast aluminium housing with toughened glass, surge protection, adjustable bracket, complete with wiring and earthing as per specification No: LF-LED/FL. | Store Room | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 4365 | 4365 | 18/01/2025 | submitted
23 | 2-1-9 | Supplying and erecting LED flood light luminaire 100 W, IP66, die cast aluminium housing with toughened glass, surge protection, adjustable bracket, complete with wiring and earthing as per specification No: LF-LED/FL. | Class Room 1 | First Floor | Each | 2 | 1 | 0 | 0 | 2 | 4365 | 8730 | 18/01/2025 | submitted
24 | 2-1-12 | Supplying and erecting LED street light luminaire 120 W, IP66 with programmable driver, surge protection up to 10 kV, complete with wiring and earthing as per specification No: LF-LED/SL. | Head Master Cabin | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 9365 | 9365 | 18/01/2025 | submitted
24 | 2-1-12 | Supplying and erecting LED street light luminaire 120 W, IP66 with programmable driver, surge protection up to 10 kV, complete with wiring and earthing as per specification No: LF-LED/SL. | Office Room 1 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 9365 | 9365 | 18/01/2025 | submitted
24 | 2-1-12 | Supplying and erecting LED street light luminaire 120 W, IP66 with programmable driver, surge protection up to 10 kV, complete with wiring and earthing as per specification No: LF-LED/SL. | Office Room 2 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 9365 | 9365 | 18/01/2025 | submitted
24 | 2-1-12 | Supplying and erecting LED street light luminaire 120 W, IP66 with programmable driver, surge protection up to 10 kV, complete with wiring and earthing as per specification No: LF-LED/SL. | Store Room | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 9365 | 9365 | 18/01/2025 | submitted
25 | 2-1-16 | Supplying and erecting LED emergency light fitting with 2 hours battery backup, 2 x 6 W LED, chargeable type, complete with wiring and earthing as per specification No: LF-EM/LT. | Head Master Cabin | Ground Floor | Each | 5 | 1 | 0 | 0 | 5 | 2915 | 14575 | 18/01/2025 | submitted
25 | 2-1-16 | Supplying and erecting LED emergency light fitting with 2 hours battery backup, 2 x 6 W LED, chargeable type, complete with wiring and earthing as per specification No: LF-EM/LT. | Office Room 1 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 2915 | 2915 | 18/01/2025 | submitted
25 | 2-1-16 | Supplying and erecting LED emergency light fitting with 2 hours battery backup, 2 x 6 W LED, chargeable type, complete with wiring and earthing as per specification No: LF-EM/LT. | Office Room 2 | Ground Floor | Each | 2 | 1 | 0 | 0 | 2 | 2915 | 5830 | 18/01/2025 | submitted
26 | 2-1-17 | Supplying and erecting LED exit sign luminaire with emergency backup 2 hours, ceiling / wall mounted, complete with wiring and earthing as per specification No: LF-EM/EX. | Head Master Cabin | Ground Floor | Each | 3 | 1 | 0 | 0 | 3 | 3000 | 9000 | 18/01/2025 | submitted
26 | 2-1-17 | Supplying and erecting LED exit sign luminaire with emergency backup 2 hours, ceiling / wall mounted, complete with wiring and earthing as per specification No: LF-EM/EX. | Office Room 1 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 3000 | 3000 | 18/01/2025 | submitted
26 | 2-1-17 | Supplying and erecting LED exit sign luminaire with emergency backup 2 hours, ceiling / wall mounted, complete with wiring and earthing as per specification No: LF-EM/EX. | Office Room 2 | Ground Floor | Each | 2 | 1 | 0 | 0 | 2 | 3000 | 6000 | 18/01/2025 | submitted
27 | 3-1-1 | Supplying and erecting ceiling fan 1200 mm sweep, 5 star rated, 230 V AC, with down rod, canopy, shackle, blades and 3 core flexible wire, complete with earthing as per specification No: FN/CF. | Head Master Cabin | Ground Floor | Each | 2 | 1 | 0 | 0 | 2 | 3245 | 6490 | 18/01/2025 | submitted
27 | 3-1-1 | Supplying and erecting ceiling fan 1200 mm sweep, 5 star rated, 230 V AC, with down rod, canopy, shackle, blades and 3 core flexible wire, complete with earthing as per specification No: FN/CF. | Office Room 1 | Ground Floor | Each | 5 | 1 | 0 | 0 | 5 | 3245 | 16225 | 18/01/2025 | submitted
27 | 3-1-1 | Supplying and erecting ceiling fan 1200 mm sweep, 5 star rated, 230 V AC, with down rod, canopy, shackle, blades and 3 core flexible wire, complete with earthing as per specification No: FN/CF. | Office Room 2 | Ground Floor | Each | 3 | 1 | 0 | 0 | 3 | 3245 | 9735 | 18/01/2025 | submitted
27 | 3-1-1 | Supplying and erecting ceiling fan 1200 mm sweep, 5 star rated, 230 V AC, with down rod, canopy, shackle, blades and 3 core flexible wire, complete with earthing as per specification No: FN/CF. | Store Room | Ground Floor | Each | 6 | 1 | 0 | 0 | 6 | 3245 | 19470 | 18/01/2025 | submitted
28 | 3-1-6 | Supplying and erecting exhaust fan 250 mm (10 inch) sweep, metal body with powder coating, shutter type, complete with wiring connections and earthing as per specification No: FN/EX. | Head Master Cabin | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 2470 | 2470 | 18/01/2025 | submitted
28 | 3-1-6 | Supplying and erecting exhaust fan 250 mm (10 inch) sweep, metal body with powder coating, shutter type, complete with wiring connections and earthing as per specification No: FN/EX. | Office Room 1 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 2470 | 2470 | 18/01/2025 | submitted
28 | 3-1-6 | Supplying and erecting exhaust fan 250 mm (10 inch) sweep, metal body with powder coating, shutter type, complete with wiring connections and earthing as per specification No: FN/EX. | Office Room 2 | Ground Floor | Each | 5 | 1 | 0 | 0 | 5 | 2470 | 12350 | 18/01/2025 | submitted
29 | 3-1-11 | Supplying and fixing MS fan hook / clamp box concealed in RCC slab for ceiling fan, with hooks, painting and necessary making good complete as per specification No: FN/HK. | Head Master Cabin | Ground Floor | Each | 6 | 1 | 0 | 0 | 6 | 275 | 1650 | 18/01/2025 | submitted
29 | 3-1-11 | Supplying and fixing MS fan hook / clamp box concealed in RCC slab for ceiling fan, with hooks, painting and necessary making good complete as per specification No: FN/HK. | Office Room 1 | Ground Floor | Each | 5 | 1 | 0 | 0 | 5 | 275 | 1375 | 18/01/2025 | submitted
29 | 3-1-11 | Supplying and fixing MS fan hook / clamp box concealed in RCC slab for ceiling fan, with hooks, painting and necessary making good complete as per specification No: FN/HK. | Office Room 2 | Ground Floor | Each | 4 | 1 | 0 | 0 | 4 | 275 | 1100 | 18/01/2025 | submitted
30 | 6-1-1 | Supplying and fixing SPN distribution board, 8 way, single door, powder coated CRCA sheet enclosure, with tinned copper bus bar, neutral link, earth link, din rail and knockouts, complete with earthing as per specification No: DB-SPN. | Head Master Cabin | Ground Floor | Each | 3 | 1 | 0 | 0 | 3 | 3935 | 11805 | 18/01/2025 | submitted
30 | 6-1-1 | Supplying and fixing SPN distribution board, 8 way, single door, powder coated CRCA sheet enclosure, with tinned copper bus bar, neutral link, earth link, din rail and knockouts, complete with earthing as per specification No: DB-SPN. | Office Room 1 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 3935 | 3935 | 18/01/2025 | submitted
31 | 6-1-3 | Supplying and fixing TPN distribution board, 8 way, double door, powder coated CRCA sheet enclosure with bus bar, neutral and earth links, complete with earthing and connections as per specification No: DB-TPN. | Head Master Cabin | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 8280 | 8280 | 18/01/2025 | submitted
31 | 6-1-3 | Supplying and fixing TPN distribution board, 8 way, double door, powder coated CRCA sheet enclosure with bus bar, neutral and earth links, complete with earthing and connections as per specification No: DB-TPN. | Office Room 1 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 8280 | 8280 | 18/01/2025 | submitted
32 | 6-2-1 | Supplying and fixing MCB single pole 6 A to 32 A, C curve, 10 kA breaking capacity, ISI marked, complete with connections as per specification No: SW/MCB. | Head Master Cabin | Ground Floor | Each | 26 | 1 | 0 | 0 | 26 | 495 | 12870 | 18/01/2025 | submitted
32 | 6-2-1 | Supplying and fixing MCB single pole 6 A to 32 A, C curve, 10 kA breaking capacity, ISI marked, complete with connections as per specification No: SW/MCB. | Office Room 1 | Ground Floor | Each | 21 | 1 | 0 | 0 | 21 | 495 | 10395 | 18/01/2025 | submitted
33 | 6-2-4 | Supplying and fixing RCCB double pole 40 A, 30 mA sensitivity, 10 kA, complete with connections and earthing as per specification No: SW/RCCB. | Head Master Cabin | Ground Floor | Each | 2 | 1 | 0 | 0 | 2 | 3305 | 6610 | 18/01/2025 | submitted
33 | 6-2-4 | Supplying and fixing RCCB double pole 40 A, 30 mA sensitivity, 10 kA, complete with connections and earthing as per specification No: SW/RCCB. | Office Room 1 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 3305 | 3305 | 18/01/2025 | submitted
33 | 6-2-4 | Supplying and fixing RCCB double pole 40 A, 30 mA sensitivity, 10 kA, complete with connections and earthing as per specification No: SW/RCCB. | Office Room 2 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 3305 | 3305 | 18/01/2025 | submitted
33 | 6-2-4 | Supplying and fixing RCCB double pole 40 A, 30 mA sensitivity, 10 kA, complete with connections and earthing as per specification No: SW/RCCB. | Store Room | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 3305 | 3305 | 18/01/2025 | submitted
33 | 6-2-4 | Supplying and fixing RCCB double pole 40 A, 30 mA sensitivity, 10 kA, complete with connections and earthing as per specification No: SW/RCCB. | Class Room 1 | First Floor | Each | 1 | 1 | 0 | 0 | 1 | 3305 | 3305 | 18/01/2025 | submitted
34 | 7-2-4 | Supplying, erecting and terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3.5 core 16 sq.mm copper conductor with glands and lugs complete as per specification No: CB-LT/CU. | Head Master Cabin | Ground Floor | m | 1 | 71.03 | 0 | 0 | 71.03 | 1045 | 74226.35 | 18/01/2025 | submitted
34 | 7-2-4 | Supplying, erecting and terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3.5 core 16 sq.mm copper conductor with glands and lugs complete as per specification No: CB-LT/CU. | Office Room 1 | Ground Floor | m | 1 | 1 | 0 | 0 | 1 | 1045 | 1045 | 18/01/2025 | submitted
34 | 7-2-4 | Supplying, erecting and terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3.5 core 16 sq.mm copper conductor with glands and lugs complete as per specification No: CB-LT/CU. | Office Room 2 | Ground Floor | m | 1 | 45.63 | 0 | 0 | 45.63 | 1045 | 47683.35 | 18/01/2025 | submitted
35 | 7-2-2 | Supplying, erecting and terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3.5 core 6 sq.mm copper conductor with glands and lugs, erected on wall / trusses / pole or laid in trench / pipe as per specification No: CB-LT/CU. | Head Master Cabin | Ground Floor | m | 1 | 10.43 | 0 | 0 | 10.43 | 470 | 4902.1 | 18/01/2025 | submitted
35 | 7-2-2 | Supplying, erecting and terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3.5 core 6 sq.mm copper conductor with glands and lugs, erected on wall / trusses / pole or laid in trench / pipe as per specification No: CB-LT/CU. | Office Room 1 | Ground Floor | m | 1 | 13.75 | 0 | 0 | 13.75 | 470 | 6462.5 | 18/01/2025 | submitted
35 | 7-2-2 | Supplying, erecting and terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3.5 core 6 sq.mm copper conductor with glands and lugs, erected on wall / trusses / pole or laid in trench / pipe as per specification No: CB-LT/CU. | Office Room 2 | Ground Floor | m | 1 | 12.69 | 0 | 0 | 12.69 | 470 | 5964.3 | 18/01/2025 | submitted
35 | 7-2-2 | Supplying, erecting and terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3.5 core 6 sq.mm copper conductor with glands and lugs, erected on wall / trusses / pole or laid in trench / pipe as per specification No: CB-LT/CU. | Store Room | Ground Floor | m | 1 | 23.81 | 0 | 0 | 23.81 | 470 | 11190.7 | 18/01/2025 | submitted
35 | 7-2-2 | Supplying, erecting and terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3.5 core 6 sq.mm copper conductor with glands and lugs, erected on wall / trusses / pole or laid in trench / pipe as per specification No: CB-LT/CU. | Class Room 1 | First Floor | m | 1 | 20.91 | 0 | 0 | 20.91 | 470 | 9827.7 | 18/01/2025 | submitted
36 | 7-4-1 | Supplying and erecting brass double compression type cable gland suitable for 20-25 mm cable with earth tag, lock nut and neoprene ring complete as per specification No: CB/ACC. | Head Master Cabin | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 355 | 355 | 18/01/2025 | submitted
36 | 7-4-1 | Supplying and erecting brass double compression type cable gland suitable for 20-25 mm cable with earth tag, lock nut and neoprene ring complete as per specification No: CB/ACC. | Office Room 1 | Ground Floor | Each | 9 | 1 | 0 | 0 | 9 | 355 | 3195 | 18/01/2025 | submitted
36 | 7-4-1 | Supplying and erecting brass double compression type cable gland suitable for 20-25 mm cable with earth tag, lock nut and neoprene ring complete as per specification No: CB/ACC. | Office Room 2 | Ground Floor | Each | 2 | 1 | 0 | 0 | 2 | 355 | 710 | 18/01/2025 | submitted
36 | 7-4-1 | Supplying and erecting brass double compression type cable gland suitable for 20-25 mm cable with earth tag, lock nut and neoprene ring complete as per specification No: CB/ACC. | Store Room | Ground Floor | Each | 4 | 1 | 0 | 0 | 4 | 355 | 1420 | 18/01/2025 | submitted
36 | 7-4-1 | Supplying and erecting brass double compression type cable gland suitable for 20-25 mm cable with earth tag, lock nut and neoprene ring complete as per specification No: CB/ACC. | Class Room 1 | First Floor | Each | 7 | 1 | 0 | 0 | 7 | 355 | 2485 | 18/01/2025 | submitted
37 | 7-4-2 | Supplying and crimping heavy duty aluminium / copper cable lug of suitable size with crimping tool and insulation sleeve complete as per specification No: CB/ACC. | Head Master Cabin | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 190 | 190 | 18/01/2025 | submitted
37 | 7-4-2 | Supplying and crimping heavy duty aluminium / copper cable lug of suitable size with crimping tool and insulation sleeve complete as per specification No: CB/ACC. | Office Room 1 | Ground Floor | Each | 12 | 1 | 0 | 0 | 12 | 190 | 2280 | 18/01/2025 | submitted
37 | 7-4-2 | Supplying and crimping heavy duty aluminium / copper cable lug of suitable size with crimping tool and insulation sleeve complete as per specification No: CB/ACC. | Office Room 2 | Ground Floor | Each | 6 | 1 | 0 | 0 | 6 | 190 | 1140 | 18/01/2025 | submitted
37 | 7-4-2 | Supplying and crimping heavy duty aluminium / copper cable lug of suitable size with crimping tool and insulation sleeve complete as per specification No: CB/ACC. | Store Room | Ground Floor | Each | 28 | 1 | 0 | 0 | 28 | 190 | 5320 | 18/01/2025 | submitted
38 | 9-1-1 | Providing earthing with galvanized iron earth plate size 60 x 60 x 0.6 cm, buried in pit with alternate layers of salt and charcoal, connected with watering pipe, funnel, GI strip up to test point and masonry chamber with CI cover, testing and recording the results as per specification No: EA-EP. | Head Master Cabin | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 13095 | 13095 | 18/01/2025 | submitted
38 | 9-1-1 | Providing earthing with galvanized iron earth plate size 60 x 60 x 0.6 cm, buried in pit with alternate layers of salt and charcoal, connected with watering pipe, funnel, GI strip up to test point and masonry chamber with CI cover, testing and recording the results as per specification No: EA-EP. | Office Room 1 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 13095 | 13095 | 18/01/2025 | submitted
38 | 9-1-1 | Providing earthing with galvanized iron earth plate size 60 x 60 x 0.6 cm, buried in pit with alternate layers of salt and charcoal, connected with watering pipe, funnel, GI strip up to test point and masonry chamber with CI cover, testing and recording the results as per specification No: EA-EP. | Office Room 2 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 13095 | 13095 | 18/01/2025 | submitted
39 | 9-1-4 | Providing maintenance free chemical earthing with 3 m long electrode, back fill compound, bentonite, test point, chamber with cover, testing and recording of earth resistance as per specification No: EA-CE. | Head Master Cabin | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 22030 | 22030 | 18/01/2025 | submitted
39 | 9-1-4 | Providing maintenance free chemical earthing with 3 m long electrode, back fill compound, bentonite, test point, chamber with cover, testing and recording of earth resistance as per specification No: EA-CE. | Office Room 1 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 22030 | 22030 | 18/01/2025 | submitted
40 | 9-2-3 | Supplying and fixing GI strip 25 x 6 mm as earth continuity conductor / earth lead with clamps, bolts, painting and connections complete as per specification No: EA-EC. | Head Master Cabin | Ground Floor | m | 1 | 20.41 | 0 | 0 | 20.41 | 275 | 5612.75 | 18/01/2025 | submitted
40 | 9-2-3 | Supplying and fixing GI strip 25 x 6 mm as earth continuity conductor / earth lead with clamps, bolts, painting and connections complete as per specification No: EA-EC. | Office Room 1 | Ground Floor | m | 1 | 4.51 | 0 | 0 | 4.51 | 275 | 1240.25 | 18/01/2025 | submitted
40 | 9-2-3 | Supplying and fixing GI strip 25 x 6 mm as earth continuity conductor / earth lead with clamps, bolts, painting and connections complete as per specification No: EA-EC. | Office Room 2 | Ground Floor | m | 1 | 9.92 | 0 | 0 | 9.92 | 275 | 2728 | 18/01/2025 | submitted
40 | 9-2-3 | Supplying and fixing GI strip 25 x 6 mm as earth continuity conductor / earth lead with clamps, bolts, painting and connections complete as per specification No: EA-EC. | Store Room | Ground Floor | m | 1 | 39.54 | 0 | 0 | 39.54 | 275 | 10873.5 | 18/01/2025 | submitted
40 | 9-2-3 | Supplying and fixing GI strip 25 x 6 mm as earth continuity conductor / earth lead with clamps, bolts, painting and connections complete as per specification No: EA-EC. | Class Room 1 | First Floor | m | 1 | 11.77 | 0 | 0 | 11.77 | 275 | 3236.75 | 18/01/2025 | submitted
41 | 9-3-1 | Supplying and erecting copper lightning protection spike / air termination rod 1 m long with base, fittings and connections to down conductor complete as per specification No: EA-LP. | Head Master Cabin | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 8815 | 8815 | 18/01/2025 | submitted
41 | 9-3-1 | Supplying and erecting copper lightning protection spike / air termination rod 1 m long with base, fittings and connections to down conductor complete as per specification No: EA-LP. | Office Room 1 | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 8815 | 8815 | 18/01/2025 | submitted
42 | 9-4-2 | Earth resistance testing with earth tester, recording of results in prescribed proforma and submission of test report as per specification No: EA/TEST. | Head Master Cabin | Ground Floor | Each | 1 | 1 | 0 | 0 | 1 | 495 | 495 | 18/01/2025 | submitted
42 | 9-4-2 | Earth resistance testing with earth tester, recording of results in prescribed proforma and submission of test report as per specification No: EA/TEST. | Office Room 1 | Ground Floor | Each | 4 | 1 | 0 | 0 | 4 | 495 | 1980 | 18/01/2025 | submitted
43 | 14-3-1 | Testing and commissioning of internal electrical installation including megger test of circuits, polarity test, earth continuity test and submission of test records per point as per specification No: TMP/TEST. | Head Master Cabin | Ground Floor | Point | 119 | 1 | 0 | 0 | 119 | 100 | 11900 | 18/01/2025 | submitted
43 | 14-3-1 | Testing and commissioning of internal electrical installation including megger test of circuits, polarity test, earth continuity test and submission of test records per point as per specification No: TMP/TEST. | Office Room 1 | Ground Floor | Point | 2 | 1 | 0 | 0 | 2 | 100 | 200 | 18/01/2025 | submitted
43 | 14-3-1 | Testing and commissioning of internal electrical installation including megger test of circuits, polarity test, earth continuity test and submission of test records per point as per specification No: TMP/TEST. | Office Room 2 | Ground Floor | Point | 189 | 1 | 0 | 0 | 189 | 100 | 18900 | 18/01/2025 | submitted
44 | 14-4-1 | Excavation of trench in ordinary soil up to 1.5 m depth for cable laying including refilling, ramming and disposal of surplus earth complete as per specification No: TMP/EXC. | Head Master Cabin | Ground Floor | m | 1 | 101.41 | 0 | 0 | 101.41 | 275 | 27887.75 | 18/01/2025 | submitted
44 | 14-4-1 | Excavation of trench in ordinary soil up to 1.5 m depth for cable laying including refilling, ramming and disposal of surplus earth complete as per specification No: TMP/EXC. | Office Room 1 | Ground Floor | m | 1 | 0.71 | 0 | 0 | 0.71 | 275 | 195.25 | 18/01/2025 | submitted
44 | 14-4-1 | Excavation of trench in ordinary soil up to 1.5 m depth for cable laying including refilling, ramming and disposal of surplus earth complete as per specification No: TMP/EXC. | Office Room 2 | Ground Floor | m | 1 | 13.2 | 0 | 0 | 13.2 | 275 | 3630 | 18/01/2025 | submitted
|  | GRAND TOTAL | [9 empty] | 1343175.35

## Deviation Statement
CSR Code | Short Description | Unit | Rate | Tendered Qty | Measured Qty | Deviation | Deviation % | Excess/Saving Amount | Alert
1-9-1 | Concealed type light / fan / bell point wiring with 1.5 sq.mm (1.5 + 1E) F… | Point | 495 | 84 | 83 | -1 | -1.19 | -495 | Saving
1-9-2 | Concealed type independent plug point wiring with 2.5 sq.mm (2.5 + 1E) FR… | Point | 605 | 22 | 22 | 0 | 0 | 0
1-9-3 | Concealed type 6 A plug point wiring with 1.5 sq.mm (2 + 1E) FRLSH copper… | Point | 540 | 18 | 18 | 0 | 0 | 0
1-9-4 | Concealed type twin light point / two way control point wiring with 1.5 sq… | Point | 765 | 12 | 12 | 0 | 0 | 0
1-9-5 | Concealed type 16 A power plug point wiring with 4.0 sq.mm (2 + 1E) FRLSH… | Point | 830 | 10 | 9 | -1 | -10 | -830 | REVIEW - beyond permitted variation
1-9-6 | Concealed type ceiling fan point wiring with 1.5 sq.mm (2 + 1E) FR copper… | Point | 630 | 16 | 16 | 0 | 0 | 0
1-9-8 | Concealed type call bell point wiring with 1.5 sq.mm (2 + 1E) FR copper wi… | Point | 390 | 4 | 4 | 0 | 0 | 0
1-9-10 | S&F modular electronic fan regulator with 2 M plate, GI box, connections a… | Each | 435 | 16 | 15 | -1 | -6.25 | -435 | Saving
1-1-1 | S&L 20 mm dia. PVC conduit concealed in wall / ceiling / slab with necessa… | m | 100 | 620 | 590.42 | -29.58 | -4.77 | -2958 | Saving
1-1-2 | S&L 25 mm dia. PVC conduit concealed in wall / ceiling / slab with necessa… | m | 125 | 340 | 327.51 | -12.49 | -3.67 | -1561.25 | Saving
1-1-4 | S&L 20 mm dia. 16 gauge rigid steel conduit on surface / concealed with co… | m | 275 | 180 | 174.34 | -5.66 | -3.14 | -1556.5 | Saving
1-1-6 | S&F GI concealed box (8 module) with cover plate for modular switches / so… | Each | 220 | 120 | 115 | -5 | -4.17 | -1100 | Saving
1-3-3 | S&E mains with 2 x 4 sq.mm FRLSH copper PVC insulated wire laid in provide… | m | 150 | 260 | 250.8 | -9.2 | -3.54 | -1380 | Saving
1-3-6 | S&E mains with 3 x 4 sq.mm FRLSH copper PVC insulated wire laid in provide… | m | 220 | 190 | 183.23 | -6.77 | -3.56 | -1489.4 | Saving
1-3-8 | S&E mains with 3 x 10 sq.mm FRLSH copper PVC insulated wire laid in provid… | m | 460 | 120 | 116.45 | -3.55 | -2.96 | -1633 | Saving
1-3-11 | S&E mains with 4 x 10 sq.mm FRLSH copper PVC insulated wire laid in provid… | m | 615 | 90 | 88.15 | -1.85 | -2.06 | -1137.75 | Saving
1-5-5 | S&F modular switch 6 A / 16 A on 2 M plate with GI box, connections and ea… | Each | 190 | 64 | 61 | -3 | -4.69 | -570 | Saving
1-5-1 | S&E recess type 3 pin plug socket 6 A with piano switch 6 A combined unit… | Each | 170 | 24 | 24 | 0 | 0 | 0
1-5-2 | S&E recess type 6 pin plug socket 16 A with switch 16 A combined unit moun… | Each | 405 | 8 | 9 | 1 | 12.5 | 405 | REVIEW - beyond permitted variation
2-1-3 | S&E LED batten luminaire 20 W, 4 ft, 6500 K, polycarbonate body with drive… | Each | 1205 | 96 | 95 | -1 | -1.04 | -1205 | Saving
2-1-1 | S&E LED panel luminaire 18 W, 1200 x 300 mm, surface mounted, 6500 K, CRCA… | Each | 2185 | 42 | 42 | 0 | 0 | 0
2-1-5 | S&E LED bulkhead luminaire 20 W, IP65, die cast aluminium body with toughe… | Each | 1695 | 12 | 12 | 0 | 0 | 0
2-1-9 | S&E LED flood light luminaire 100 W, IP66, die cast aluminium housing with… | Each | 4365 | 8 | 10 | 2 | 25 | 8730 | CRITICAL - variation approval required
2-1-12 | S&E LED street light luminaire 120 W, IP66 with programmable driver, surge… | Each | 9365 | 4 | 4 | 0 | 0 | 0
2-1-16 | S&E LED emergency light fitting with 2 hours battery backup, 2 x 6 W LED,… | Each | 2915 | 8 | 8 | 0 | 0 | 0
2-1-17 | S&E LED exit sign luminaire with emergency backup 2 hours, ceiling / wall… | Each | 3000 | 6 | 6 | 0 | 0 | 0
3-1-1 | S&E ceiling fan 1200 mm sweep, 5 star rated, 230 V AC, with down rod, cano… | Each | 3245 | 16 | 16 | 0 | 0 | 0
3-1-6 | S&E exhaust fan 250 mm (10 inch) sweep, metal body with powder coating, sh… | Each | 2470 | 6 | 7 | 1 | 16.67 | 2470 | REVIEW - beyond permitted variation
3-1-11 | S&F MS fan hook / clamp box concealed in RCC slab for ceiling fan, with ho… | Each | 275 | 16 | 15 | -1 | -6.25 | -275 | Saving
6-1-1 | S&F SPN distribution board, 8 way, single door, powder coated CRCA sheet e… | Each | 3935 | 4 | 4 | 0 | 0 | 0
6-1-3 | S&F TPN distribution board, 8 way, double door, powder coated CRCA sheet e… | Each | 8280 | 2 | 2 | 0 | 0 | 0
6-2-1 | S&F MCB single pole 6 A to 32 A, C curve, 10 kA breaking capacity, ISI mar… | Each | 495 | 48 | 47 | -1 | -2.08 | -495 | Saving
6-2-4 | S&F RCCB double pole 40 A, 30 mA sensitivity, 10 kA, complete with connect… | Each | 3305 | 6 | 6 | 0 | 0 | 0
7-2-4 | S/E&Term FR XLPE insulated, galvanised steel formed wire armoured (strip)… | m | 1045 | 120 | 117.66 | -2.34 | -1.95 | -2445.3 | Saving
7-2-2 | S/E&Term FR XLPE insulated, galvanised steel formed wire armoured (strip)… | m | 470 | 85 | 81.59 | -3.41 | -4.01 | -1602.7 | Saving
7-4-1 | S&E brass double compression type cable gland suitable for 20-25 mm cable… | Each | 355 | 24 | 23 | -1 | -4.17 | -355 | Saving
7-4-2 | Supplying and crimping heavy duty aluminium / copper cable lug of suitable… | Each | 190 | 48 | 47 | -1 | -2.08 | -190 | Saving
9-1-1 | Prov. earthing with galvanized iron earth plate size 60 x 60 x 0.6 cm, bur… | Each | 13095 | 3 | 3 | 0 | 0 | 0
9-1-4 | Prov. maintenance free chemical earthing with 3 m long electrode, back fil… | Each | 22030 | 2 | 2 | 0 | 0 | 0
9-2-3 | S&F GI strip 25 x 6 mm as earth continuity conductor / earth lead with cla… | m | 275 | 90 | 86.15 | -3.85 | -4.28 | -1058.75 | Saving
9-3-1 | S&E copper lightning protection spike / air termination rod 1 m long with… | Each | 8815 | 2 | 2 | 0 | 0 | 0
9-4-2 | Earth resistance testing with earth tester, recording of results in prescr… | Each | 495 | 5 | 5 | 0 | 0 | 0
14-3-1 | Testing and commissioning of internal electrical installation including me… | Point | 100 | 320 | 310 | -10 | -3.12 | -1000 | Saving
14-4-1 | Excavation of trench in ordinary soil up to 1.5 m depth for cable laying i… | m | 275 | 120 | 115.32 | -4.68 | -3.9 | -1287 | Saving

## Estimate Items
Item No. | CSR Code | Description (Master CSR) | Unit | Rate | Tendered Qty | Tendered Amount | Source | Non-Schedule | Match Method | Confidence
1 | 1-9-1 | Concealed type light / fan / bell point wiring with 1.5 sq.mm (1.5 + 1E) FR grade copper wire in provided concealed pipes, terminating on modular accessories in box, including earthing and required accessories as per specification No: WG-PW/CW. | Point | 495 | 84 | 41580 | estimate |  | row-end-numeric | 0.94
2 | 1-9-2 | Concealed type independent plug point wiring with 2.5 sq.mm (2.5 + 1E) FR grade copper wire in provided concealed pipes with modular socket, switch and earthing as per specification No: WG-PW/CW. | Point | 605 | 22 | 13310 | estimate |  | row-end-numeric | 0.94
3 | 1-9-3 | Concealed type 6 A plug point wiring with 1.5 sq.mm (2 + 1E) FRLSH copper wire, modular accessories, box and earthing as per specification No: WG-PW/CW. | Point | 540 | 18 | 9720 | estimate |  | row-end-numeric | 0.94
4 | 1-9-4 | Concealed type twin light point / two way control point wiring with 1.5 sq.mm (3 + 1E) FR copper wire, two modular switches, box, earthing and accessories as per specification No: WG-PW/CW. | Point | 765 | 12 | 9180 | estimate |  | row-end-numeric | 0.94
5 | 1-9-5 | Concealed type 16 A power plug point wiring with 4.0 sq.mm (2 + 1E) FRLSH copper wire, modular socket with switch, box and earthing as per specification No: WG-PW/CW. | Point | 830 | 10 | 8300 | estimate |  | row-end-numeric | 0.94
6 | 1-9-6 | Concealed type ceiling fan point wiring with 1.5 sq.mm (2 + 1E) FR copper wire, fan hook / clamp box on RCC slab, modular regulator, earthing and accessories as per specification No: WG-PW/CW. | Point | 630 | 16 | 10080 | estimate |  | row-end-numeric | 0.94
7 | 1-9-8 | Concealed type call bell point wiring with 1.5 sq.mm (2 + 1E) FR copper wire, bell push and earthing in concealed box as per specification No: WG-PW/CW. | Point | 390 | 4 | 1560 | estimate |  | row-end-numeric | 0.94
8 | 1-9-10 | Supplying and fixing modular electronic fan regulator with 2 M plate, GI box, connections and earthing complete as per specification No: WG-PS/MOD. | Each | 435 | 16 | 6960 | estimate |  | row-end-numeric | 0.94
9 | 1-1-1 | Supplying and laying 20 mm dia. PVC conduit concealed in wall / ceiling / slab with necessary bends, couplers, junction boxes, cutting and making good the wall complete as per specification No: WG-CP/PVC. | m | 100 | 620 | 62000 | estimate |  | row-end-numeric | 0.94
10 | 1-1-2 | Supplying and laying 25 mm dia. PVC conduit concealed in wall / ceiling / slab with necessary bends, couplers, junction boxes, cutting and making good the wall complete as per specification No: WG-CP/PVC. | m | 125 | 340 | 42500 | estimate |  | row-end-numeric | 0.94
11 | 1-1-4 | Supplying and laying 20 mm dia. 16 gauge rigid steel conduit on surface / concealed with couplers, bends, hooks, saddles, painting with two coats of anti-corrosive paint, earthing continuity complete as per specification No: WG-CP/RSC. | m | 275 | 180 | 49500 | estimate |  | row-end-numeric | 0.94
12 | 1-1-6 | Supplying and fixing GI concealed box (8 module) with cover plate for modular switches / sockets including cutting and making good complete as per specification No: WG-CP/MOD. | Each | 220 | 120 | 26400 | estimate |  | row-end-numeric | 0.94
13 | 1-3-3 | Supplying and erecting mains with 2 x 4 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | m | 150 | 260 | 39000 | estimate |  | row-end-numeric | 0.94
14 | 1-3-6 | Supplying and erecting mains with 3 x 4 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | m | 220 | 190 | 41800 | estimate |  | row-end-numeric | 0.94
15 | 1-3-8 | Supplying and erecting mains with 3 x 10 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | m | 460 | 120 | 55200 | estimate |  | row-end-numeric | 0.94
16 | 1-3-11 | Supplying and erecting mains with 4 x 10 sq.mm FRLSH copper PVC insulated wire laid in provided conduit / trunking / inside pole / bus bars or any other places as per specification No: WG-MA/BW. | m | 615 | 90 | 55350 | estimate |  | row-end-numeric | 0.94
17 | 1-5-5 | Supplying and fixing modular switch 6 A / 16 A on 2 M plate with GI box, connections and earthing complete as per specification No: WG-PS/MOD. | Each | 190 | 64 | 12160 | estimate |  | row-end-numeric | 0.94
18 | 1-5-1 | Supplying and erecting recess type 3 pin plug socket 6 A with piano switch 6 A combined unit erected on polished double wooden block / folded sheet box complete as per specification No: WG-PS/RC. | Each | 170 | 24 | 4080 | estimate |  | row-end-numeric | 0.94
19 | 1-5-2 | Supplying and erecting recess type 6 pin plug socket 16 A with switch 16 A combined unit mounted on sheet steel box with earth terminal complete as per specification No: WG-PS/RC. | Each | 405 | 8 | 3240 | estimate |  | row-end-numeric | 0.94
20 | 2-1-3 | Supplying and erecting LED batten luminaire 20 W, 4 ft, 6500 K, polycarbonate body with driver, complete with connections and earthing as per specification No: LF-LED/BTN. | Each | 1205 | 96 | 115680 | estimate |  | row-end-numeric | 0.94
21 | 2-1-1 | Supplying and erecting LED panel luminaire 18 W, 1200 x 300 mm, surface mounted, 6500 K, CRCA sheet housing with diffuser, complete with driver, connections and earthing as per specification No: LF-LED/PNL. | Each | 2185 | 42 | 91770 | estimate |  | row-end-numeric | 0.94
22 | 2-1-5 | Supplying and erecting LED bulkhead luminaire 20 W, IP65, die cast aluminium body with toughened glass, complete with driver, connections and earthing as per specification No: LF-LED/BHD. | Each | 1695 | 12 | 20340 | estimate |  | row-end-numeric | 0.94
23 | 2-1-9 | Supplying and erecting LED flood light luminaire 100 W, IP66, die cast aluminium housing with toughened glass, surge protection, adjustable bracket, complete with wiring and earthing as per specification No: LF-LED/FL. | Each | 4365 | 8 | 34920 | estimate |  | row-end-numeric | 0.94
24 | 2-1-12 | Supplying and erecting LED street light luminaire 120 W, IP66 with programmable driver, surge protection up to 10 kV, complete with wiring and earthing as per specification No: LF-LED/SL. | Each | 9365 | 4 | 37460 | estimate |  | row-end-numeric | 0.94
25 | 2-1-16 | Supplying and erecting LED emergency light fitting with 2 hours battery backup, 2 x 6 W LED, chargeable type, complete with wiring and earthing as per specification No: LF-EM/LT. | Each | 2915 | 8 | 23320 | estimate |  | row-end-numeric | 0.94
26 | 2-1-17 | Supplying and erecting LED exit sign luminaire with emergency backup 2 hours, ceiling / wall mounted, complete with wiring and earthing as per specification No: LF-EM/EX. | Each | 3000 | 6 | 18000 | estimate |  | row-end-numeric | 0.94
27 | 3-1-1 | Supplying and erecting ceiling fan 1200 mm sweep, 5 star rated, 230 V AC, with down rod, canopy, shackle, blades and 3 core flexible wire, complete with earthing as per specification No: FN/CF. | Each | 3245 | 16 | 51920 | estimate |  | row-end-numeric | 0.94
28 | 3-1-6 | Supplying and erecting exhaust fan 250 mm (10 inch) sweep, metal body with powder coating, shutter type, complete with wiring connections and earthing as per specification No: FN/EX. | Each | 2470 | 6 | 14820 | estimate |  | row-end-numeric | 0.94
29 | 3-1-11 | Supplying and fixing MS fan hook / clamp box concealed in RCC slab for ceiling fan, with hooks, painting and necessary making good complete as per specification No: FN/HK. | Each | 275 | 16 | 4400 | estimate |  | row-end-numeric | 0.94
30 | 6-1-1 | Supplying and fixing SPN distribution board, 8 way, single door, powder coated CRCA sheet enclosure, with tinned copper bus bar, neutral link, earth link, din rail and knockouts, complete with earthing as per specification No: DB-SPN. | Each | 3935 | 4 | 15740 | estimate |  | row-end-numeric | 0.94
31 | 6-1-3 | Supplying and fixing TPN distribution board, 8 way, double door, powder coated CRCA sheet enclosure with bus bar, neutral and earth links, complete with earthing and connections as per specification No: DB-TPN. | Each | 8280 | 2 | 16560 | estimate |  | row-end-numeric | 0.94
32 | 6-2-1 | Supplying and fixing MCB single pole 6 A to 32 A, C curve, 10 kA breaking capacity, ISI marked, complete with connections as per specification No: SW/MCB. | Each | 495 | 48 | 23760 | estimate |  | row-end-numeric | 0.94
33 | 6-2-4 | Supplying and fixing RCCB double pole 40 A, 30 mA sensitivity, 10 kA, complete with connections and earthing as per specification No: SW/RCCB. | Each | 3305 | 6 | 19830 | estimate |  | row-end-numeric | 0.94
34 | 7-2-4 | Supplying, erecting and terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3.5 core 16 sq.mm copper conductor with glands and lugs complete as per specification No: CB-LT/CU. | m | 1045 | 120 | 125400 | estimate |  | row-end-numeric | 0.94
35 | 7-2-2 | Supplying, erecting and terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3.5 core 6 sq.mm copper conductor with glands and lugs, erected on wall / trusses / pole or laid in trench / pipe as per specification No: CB-LT/CU. | m | 470 | 85 | 39950 | estimate |  | row-end-numeric | 0.94
36 | 7-4-1 | Supplying and erecting brass double compression type cable gland suitable for 20-25 mm cable with earth tag, lock nut and neoprene ring complete as per specification No: CB/ACC. | Each | 355 | 24 | 8520 | estimate |  | row-end-numeric | 0.94
37 | 7-4-2 | Supplying and crimping heavy duty aluminium / copper cable lug of suitable size with crimping tool and insulation sleeve complete as per specification No: CB/ACC. | Each | 190 | 48 | 9120 | estimate |  | row-end-numeric | 0.94
38 | 9-1-1 | Providing earthing with galvanized iron earth plate size 60 x 60 x 0.6 cm, buried in pit with alternate layers of salt and charcoal, connected with watering pipe, funnel, GI strip up to test point and masonry chamber with CI cover, testing and recording the results as per specification No: EA-EP. | Each | 13095 | 3 | 39285 | estimate |  | row-end-numeric | 0.94
39 | 9-1-4 | Providing maintenance free chemical earthing with 3 m long electrode, back fill compound, bentonite, test point, chamber with cover, testing and recording of earth resistance as per specification No: EA-CE. | Each | 22030 | 2 | 44060 | estimate |  | row-end-numeric | 0.94
40 | 9-2-3 | Supplying and fixing GI strip 25 x 6 mm as earth continuity conductor / earth lead with clamps, bolts, painting and connections complete as per specification No: EA-EC. | m | 275 | 90 | 24750 | estimate |  | row-end-numeric | 0.94
41 | 9-3-1 | Supplying and erecting copper lightning protection spike / air termination rod 1 m long with base, fittings and connections to down conductor complete as per specification No: EA-LP. | Each | 8815 | 2 | 17630 | estimate |  | row-end-numeric | 0.94
42 | 9-4-2 | Earth resistance testing with earth tester, recording of results in prescribed proforma and submission of test report as per specification No: EA/TEST. | Each | 495 | 5 | 2475 | estimate |  | row-end-numeric | 0.94
43 | 14-3-1 | Testing and commissioning of internal electrical installation including megger test of circuits, polarity test, earth continuity test and submission of test records per point as per specification No: TMP/TEST. | Point | 100 | 320 | 32000 | estimate |  | row-end-numeric | 0.94
44 | 14-4-1 | Excavation of trench in ordinary soil up to 1.5 m depth for cable laying including refilling, ramming and disposal of surplus earth complete as per specification No: TMP/EXC. | m | 275 | 120 | 33000 | estimate |  | row-end-numeric | 0.94